## Notes and Versions
Road tunnel quadratics spreadsheet versioning

v1	Nov 2020. First version.
v1.1	Dec 2020. Corrected the selection of which quadratic to use at slow vehicle speeds, added a note about density 1.2 kg/m3.
v1.2	Apr 2021. Corrected errors in the sanity check calculation when the traffic blockage correction was active. Altered the text descriptions of the range and sanity checks to the correct rows. Modified a logic test that works in LibreOffice but fails in Excel to a test that works in both programs. Modified the error checks to catch more types of erroneous input.

Notes for use (in no particular order)

1)	This spreadsheet solves steady-state incompressible flow in a road tunnel with friction, portal losses,
	stationary/moving traffic, portal pressure differences and jet fans. It follows the classical approach
	given in PIARC documents, Woods Practical Guide to Fan Engineering and many BHR conference papers.

2)	If you have stationary traffic, you must set vehicle densities (veh/km). If you have moving traffic, you
	must set vehicle flowrates (veh/hr). The descriptors and units change according to whether it is stationary
	or moving traffic, but it is easy to forget.

3)	The traffic speed must be zero or positive. The spreadsheet could be extended to handle cases with
	negative traffic speeds, but a simple spreadsheet is easier to prove correct. A more complex spreadsheet
	would be harder to prove wrong.

4)	The spreadsheet does not consider area changes, friction factors varying with air velocity, or density changes.

5)	You must set which friction factor type you want to use, Darcy friction factor λ or Fanning friction
	factor c_f (λ = 4 c_f). If you are unsure about the difference between them, read “friction-rant.pdf”
	at https://github.com/ECB2020/Hobyah/tree/master/documentation

6)	The equations it uses are those in section IV of PIARC report 05.02.B (1995). That report is available
	for free on PIARC's website (piarc.org) if you register your email with PIARC (also free).

7)	The basic equation that the spreadsheet solves is

8)	Where we have positive v_t, the absolute value term |v_v – v_t| means that we have to split into two quadratics,
	one for use when the traffic speed is higher than the airspeed, one for use when it is lower. Only the sign of
	the traffic term changes.

9)	In the rare case where the pressure difference or reverse jet fans overpower the traffic piston effect and
	air blows backwards through the tunnel (negative v_t) a third equation is needed. In this case we do not need
	the absolute value term, we can solve one quadratic equation with the sign of the friction term changed.

10)	If you want the jet fans to blow against the direction of traffic, set the jet van velocity negative. Do
	not set the count of jet fans negative or the static thrust negative – they will not be accepted as valid input.

11)	The base density of the spreadsheet is 1.2 kg/m³. This is used to convert the wind and jet fan data into
	the same form as traffic drag and friction.

12)	The spreadsheet has sanity checks on the input data. Text inputs (“Y”, “N”, “Darcy”, “Fanning”) are
	not case-sensitive but it will complain if non-valid text is entered. It checks that number inputs are
	numbers and are they in the correct range. With impossible entries (like negative tunnel area)
	the spreadsheet will state that it can't calculate due to dud tunnel geometry. Similar messages
	appear for dud jet fan input, dud wind and dud traffic data.

13)	If you manage to get an unedited version of the spreadsheet to tell you that it can't calculate due
	to “dud equations” then please get in touch with me. You've found a corner case that I missed during
	testing. The “dud equations” error message is one that I wrote while developing the spreadsheet so
	that I could track down all the errors I made while writing it. So be aware that if you start editing the
	equations to extend the spreadsheet's capabilities, the message “dud equations” will likely appear.

## quadratics
Slug flow in a simple road tunnel by quadratic equations. Solution of the equations
in section IV of PIARC report 05.02.B, “Vehicle emissions, air demand, environment,
longitudinal ventilation”. Handles stationary traffic, moving traffic (vehicle speed must
not be negative), jet fans and wind. Selects the solution from a range of different
quadratics, depending on the inputs.
Slug flow spreadsheet v1.2					'slug-flow-quadratic-020.ods'#$quadratics
Single tunnel of constant area with losses, friction, jet fans, traffic drag and					Intermediate calculations (not printed)
portal pressures.					Friction term	1.152	—
					Car density	170	veh/km
					LCV density	30	veh/km
					HGV density	40	veh/km
					Car term	0.590277777777778	—		Fixed loss term	2.652	—	Sanity checks of the input data (not printed)
		Tunnel geometry input					Traffic input			LCV term	0.510396975425331	—		Wind term	16.667	m²/s²			Check of values in the tunnel terms				Check of values in the traffic terms
	Length	200	m			Traffic speed (+ve)	10	km/h		HGV term	0.991735537190083	—		Traffic term	2.092	—			'=AND(ISNUMBER(B14), B14 >= 0)	TRUE			'=AND(ISNUMBER(F14), F14 >= 0)	TRUE
	Area	50	m²			Car flowrate	1700	cars/hr		Traffic speed	2.77777777777778	m/s		Jet fan term	0.608	m/s			'=AND(ISNUMBER(B15), B15 > 0)	TRUE			'=AND(ISNUMBER(F15), F15 >= 0)	TRUE
	Perimeter	32	m			LCV flowrate	300	LCVs/hr			Calculation (vehicles slower than air)				Check calc of pressures				'=AND(ISNUMBER(B16), B16 > 0)	TRUE			'=AND(ISNUMBER(F16), F16 >= 0)	TRUE
	Friction type	Darcy	(Darcy/Fanning)			HGV flowrate	400	HGVs/hr		A	-4.74441029039319	—		Friction pressure	0.00	Pa					'=AND(ISNUMBER(F17), F17 >= 0)	TRUE
	Darcy fricfac λ	0.036	—			Car area	2	m²		B	11.0161682799622	m/s		Wind pressure	-10.00	Pa			'=OR(B17 = "Fanning", B17 = "Darcy")	TRUE			'=AND(ISNUMBER(F18), F18 > 0)	TRUE
	Left portal loss	0.5	—			Car drag factor	0.4	—		C	-14.5618077962438	m²/s²		Traffic pressure	9.69	Pa			'=AND(ISNUMBER(B18), B18 >= 0)	TRUE			'=AND(ISNUMBER(F19), F19 > 0)	TRUE
	Right portal loss	1	—			LCV area	4	m²		det	-154.992799448462	m/s		Jet fan pressure	10.95	Pa			'=AND(ISNUMBER(B19), B19 >= 0)	TRUE			'=AND(ISNUMBER(F20), F20 > 0)	TRUE
	D_h (info only, not used)	6.25	m			LCV drag factor	0.9	—		v	0.00	m/s		Sum of pressures (or 42)	10.64	Pa			'=AND(ISNUMBER(B20), B20 >= 0)	TRUE			'=AND(ISNUMBER(F21), F21 > 0)	TRUE
					HGV area	6	m²					Use this result?	FALSE				Valid fixed losses?	TRUE			'=AND(ISNUMBER(F22), F22 > 0)	TRUE
		Wind input				HGV drag factor	0.8	—			Calculation (vehicles faster than air)				Check calc of pressures				Check of values in the wind terms				'=AND(ISNUMBER(F23), F23 > 0)	TRUE
	P at left portal	0	Pa			Blockage correction?	Y	(Y/N)		A	-0.55958970960681	—		Friction pressure	-2.96	Pa			'=ISNUMBER(B24)	TRUE			'=OR(F24 = "Y", F24 = "N")	TRUE
	P at right portal	10	Pa					B	-12.2328349466288	m/s		Wind pressure	-10.00	Pa			'=ISNUMBER(B25)	TRUE			Valid traffic terms?	TRUE
					C	17.7284744629104	m²/s²		Traffic pressure	2.51	Pa			Valid wind?	TRUE
		Jet fan input					det	189.32493833735	m/s		Jet fan pressure	10.45	Pa			Check of values in the jet fan terms
	Count of fans	1	—		Calculation (vehicles faster than air)					v	1.36	m/s		Sum of pressures (or 42)	0.00	Pa			'=AND(ISNUMBER(B28), B28 >= 0)	TRUE
	Static thrust	730	N at 1.2 kg/m³			Air velocity	1.36	m/s					Use this result?	TRUE				'=AND(ISNUMBER(B29), B29 >= 0)	TRUE
	Jet velocity	30	m/s			Volume flow	68.2	m³/s			Calculation (reverse airflow)				Check calc of pressures				'=ISNUMBER(B30)	TRUE
	Installation efficiency	0.75	—					A	4.74441029039319	—		Friction pressure	159.12	Pa			'=AND(ISNUMBER(B31), B31 >= 0)	TRUE
					Independent check calc of pressures					B	-12.2328349466288	m/s		Wind pressure	10.00	Pa			Valid jet fans?	TRUE
					Friction pressure	-3.0	Pa		C	17.7284744629104	m²/s²		Traffic pressure	65.48	Pa					Valid input?	TRUE
					Wind pressure	-10.0	Pa		det	-186.802375867757	m/s		Jet fan pressure	-7.30	Pa					Reason for invalid input:	dud equations
					Traffic pressure	2.5	Pa		v	10.00	m/s		Sum of pressures (or 42)	227.30	Pa
					Jet fan pressure	10.5	Pa					Use this result?	FALSE
					Sum of pressures	0.0	Pa

					A function to remove the path of a sheet tab name in LibreOffice. This is fragile.
					Filename:	'file:///Users/ecb/Documents/sandboxes/Hobyah/slug-flow-quadratic-020.ods'#$quadratics
					Directory separator:	/
					Now strip off up to 100 strings ending in the directory separator.
					1st pass	//Users/ecb/Documents/sandboxes/Hobyah/slug-flow-quadratic-020.ods'#$quadratics
					2nd	/Users/ecb/Documents/sandboxes/Hobyah/slug-flow-quadratic-020.ods'#$quadratics
					3rd	Users/ecb/Documents/sandboxes/Hobyah/slug-flow-quadratic-020.ods'#$quadratics
					and so on.	ecb/Documents/sandboxes/Hobyah/slug-flow-quadratic-020.ods'#$quadratics
					Documents/sandboxes/Hobyah/slug-flow-quadratic-020.ods'#$quadratics
					sandboxes/Hobyah/slug-flow-quadratic-020.ods'#$quadratics
					Hobyah/slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					slug-flow-quadratic-020.ods'#$quadratics
					Spreadsheet name in LibreOffice:	'slug-flow-quadratic-020.ods'#$quadratics
					Spreadsheet name in Excel:	#VALUE!
					Which program is editing this spreadsheet?	LibreOffice
					Spreadsheet name to use:	'slug-flow-quadratic-020.ods'#$quadratics

## licence
Licence
Copyright (c) 2020-2021, Ewan Bennett (ewanbennett@fastmail.com)

All rights reserved.

Released under the BSD 2-clause licence (SPDX identifier: BSD-2-Clause):

Redistribution and use in source and binary forms, with or without modification, are
permitted provided that the following conditions are met:

1	Redistributions of source code must retain the above copyright notice, this list
	of conditions and the following disclaimer.

2	Redistributions in binary form must reproduce the above copyright notice, this
	list of conditions and the following disclaimer in the documentation and/or
	other materials provided with the distribution.

THIS SOFTWARE IS PROVIDED BY THE COPYRIGHT HOLDERS AND CONTRIBUTORS "AS
IS” AND ANY EXPRESS OR IMPLIED WARRANTIES, INCLUDING, BUT NOT LIMITED TO,
THE IMPLIED WARRANTIES OF MERCHANTABILITY AND FITNESS FOR A PARTICULAR
PURPOSE ARE DISCLAIMED. IN NO EVENT SHALL THE COPYRIGHT HOLDER OR
CONTRIBUTORS BE LIABLE FOR ANY DIRECT, INDIRECT, INCIDENTAL, SPECIAL,
EXEMPLARY, OR CONSEQUENTIAL DAMAGES (INCLUDING, BUT NOT LIMITED TO,
PROCUREMENT OF SUBSTITUTE GOODS OR SERVICES; LOSS OF USE, DATA, OR
PROFITS; OR BUSINESS INTERRUPTION) HOWEVER CAUSED AND ON ANY THEORY OF
LIABILITY, WHETHER IN CONTRACT, STRICT LIABILITY, OR TORT (INCLUDING
NEGLIGENCE OR OTHERWISE) ARISING IN ANY WAY OUT OF THE USE OF THIS
SOFTWARE, EVEN IF ADVISED OF THE POSSIBILITY OF SUCH DAMAGE.