## Notes and Versions
Road tunnel quadratics spreadsheet versioning
v1 | Nov 2020. First version.
v1.1 | Dec 2020. Corrected the selection of which quadratic to use at slow vehicle speeds, added a note about density 1.2 kg/m3.
v1.2 | Apr 2021. Corrected errors in the sanity check calculation when the traffic blockage correction was active. Altered the text descriptions of the range and sanity checks to the correct rows. Modified a logic test that works in LibreOffice but fails in Excel to a test that works in both programs. Modified the error checks to catch more types of erroneous input.
Notes for use (in no particular order)
1) | This spreadsheet solves steady-state incompressible flow in a road tunnel with friction, portal losses,
stationary/moving traffic, portal pressure differences and jet fans. It follows the classical approach
given in PIARC documents, Woods Practical Guide to Fan Engineering and many BHR conference papers.
2) | If you have stationary traffic, you must set vehicle densities (veh/km). If you have moving traffic, you
must set vehicle flowrates (veh/hr). The descriptors and units change according to whether it is stationary
or moving traffic, but it is easy to forget.
3) | The traffic speed must be zero or positive. The spreadsheet could be extended to handle cases with
negative traffic speeds, but a simple spreadsheet is easier to prove correct. A more complex spreadsheet
would be harder to prove wrong.
4) | The spreadsheet does not consider area changes, friction factors varying with air velocity, or density changes.
5) | You must set which friction factor type you want to use, Darcy friction factor λ or Fanning friction
factor c_f (λ = 4 c_f). If you are unsure about the difference between them, read “friction-rant.pdf”
at https://github.com/ECB2020/Hobyah/tree/master/documentation
6) | The equations it uses are those in section IV of PIARC report 05.02.B (1995). That report is available
for free on PIARC's website (piarc.org) if you register your email with PIARC (also free).
7) | The basic equation that the spreadsheet solves is
8) | Where we have positive v_t, the absolute value term ¦v_v – v_t¦ means that we have to split into two quadratics,
one for use when the traffic speed is higher than the airspeed, one for use when it is lower. Only the sign of
the traffic term changes.
9) | In the rare case where the pressure difference or reverse jet fans overpower the traffic piston effect and
air blows backwards through the tunnel (negative v_t) a third equation is needed. In this case we do not need
the absolute value term, we can solve one quadratic equation with the sign of the friction term changed.
10) | If you want the jet fans to blow against the direction of traffic, set the jet van velocity negative. Do
not set the count of jet fans negative or the static thrust negative – they will not be accepted as valid input.
11) | The base density of the spreadsheet is 1.2 kg/m³. This is used to convert the wind and jet fan data into
the same form as traffic drag and friction.
12) | The spreadsheet has sanity checks on the input data. Text inputs (“Y”, “N”, “Darcy”, “Fanning”) are
not case-sensitive but it will complain if non-valid text is entered. It checks that number inputs are
numbers and are they in the correct range. With impossible entries (like negative tunnel area)
the spreadsheet will state that it can't calculate due to dud tunnel geometry. Similar messages
appear for dud jet fan input, dud wind and dud traffic data.
13) | If you manage to get an unedited version of the spreadsheet to tell you that it can't calculate due
to “dud equations” then please get in touch with me. You've found a corner case that I missed during
testing. The “dud equations” error message is one that I wrote while developing the spreadsheet so
that I could track down all the errors I made while writing it. So be aware that if you start editing the
equations to extend the spreadsheet's capabilities, the message “dud equations” will likely appear.

## quadratics
Slug flow in a simple road tunnel by quadratic equations. Solution of the equations
in section IV of PIARC report 05.02.B, “Vehicle emissions, air demand, environment,
longitudinal ventilation”. Handles stationary traffic, moving traffic (vehicle speed must
not be negative), jet fans and wind. Selects the solution from a range of different
quadratics, depending on the inputs.
Slug flow spreadsheet v1.2 | [6 empty] | [slug-flow-quadratic-020.xlsx]quadratics
Single tunnel of constant area with losses, friction, jet fans, traffic drag and | [7 empty] | Intermediate calculations (not printed)
portal pressures. | [7 empty] | Friction term | 1.152 | —
[8 empty] | Car density | 170 | veh/km
[8 empty] | LCV density | 30 | veh/km
[8 empty] | HGV density | 40 | veh/km
[8 empty] | Car term | 0.59028 | — |  | Fixed loss term | 2.652 | — | Sanity checks of the input data (not printed)
|  | Tunnel geometry input |  |  |  | Traffic input |  | LCV term | 0.5104 | — |  | Wind term | 16.6667 | m²/s² |  | Check of values in the tunnel terms |  |  |  | Check of values in the traffic terms
| Length | 200 | m |  | Traffic speed (+ve) | 10 | km/h | HGV term | 0.99174 | — |  | Traffic term | 2.0924 | — |  | '=AND(ISNUMBER(B14), B14 >= 0) | TRUE |  |  | '=AND(ISNUMBER(F14), F14 >= 0) | TRUE
| Area | 50 | m² |  | Car flowrate | 1700 | cars/hr | Traffic speed | 2.7778 | m/s |  | Jet fan term | 0.60833 | m/s |  | '=AND(ISNUMBER(B15), B15 > 0) | TRUE |  |  | '=AND(ISNUMBER(F15), F15 >= 0) | TRUE
| Perimeter | 32 | m |  | LCV flowrate | 300 | LCVs/hr |  | Calculation (vehicles slower than air) |  |  |  | Check calc of pressures |  |  | '=AND(ISNUMBER(B16), B16 > 0) | TRUE |  |  | '=AND(ISNUMBER(F16), F16 >= 0) | TRUE
| Friction type | Darcy | (Darcy/Fanning) |  | HGV flowrate | 400 | HGVs/hr | A | -4.7444 | — |  | Friction pressure | 0 | Pa | [5 empty] | '=AND(ISNUMBER(F17), F17 >= 0) | TRUE
| Darcy fricfac λ | 0.036 | — |  | Car area | 2 | m² | B | 11.0162 | m/s |  | Wind pressure | -10 | Pa |  | '=OR(B17 = "Fanning", B17 = "Darcy") | TRUE |  |  | '=AND(ISNUMBER(F18), F18 > 0) | TRUE
| Left portal loss | 0.5 | — |  | Car drag factor | 0.4 | — | C | -14.5618 | m²/s² |  | Traffic pressure | 9.6871 | Pa |  | '=AND(ISNUMBER(B18), B18 >= 0) | TRUE |  |  | '=AND(ISNUMBER(F19), F19 > 0) | TRUE
| Right portal loss | 1 | — |  | LCV area | 4 | m² | det | -154.9928 | m/s |  | Jet fan pressure | 10.95 | Pa |  | '=AND(ISNUMBER(B19), B19 >= 0) | TRUE |  |  | '=AND(ISNUMBER(F20), F20 > 0) | TRUE
| D_h (info only, not used) | 6.25 | m |  | LCV drag factor | 0.9 | — | v | 0 | m/s |  | Sum of pressures (or 42) | 10.6371 | Pa |  | '=AND(ISNUMBER(B20), B20 >= 0) | TRUE |  |  | '=AND(ISNUMBER(F21), F21 > 0) | TRUE
[5 empty] | HGV area | 6 | m² |  |  |  |  | Use this result? | FALSE |  |  | Valid fixed losses? | TRUE |  |  | '=AND(ISNUMBER(F22), F22 > 0) | TRUE
|  | Wind input |  |  | HGV drag factor | 0.8 | — |  | Calculation (vehicles faster than air) |  |  |  | Check calc of pressures |  |  | Check of values in the wind terms |  |  |  | '=AND(ISNUMBER(F23), F23 > 0) | TRUE
| P at left portal | 0 | Pa |  | Blockage correction? | Y | (Y/N) | A | -0.55959 | — |  | Friction pressure | -2.961 | Pa |  | '=ISNUMBER(B24) | TRUE |  |  | '=OR(F24 = "Y", F24 = "N") | TRUE
| P at right portal | 10 | Pa |  |  |  |  | B | -12.2328 | m/s |  | Wind pressure | -10 | Pa |  | '=ISNUMBER(B25) | TRUE |  |  | Valid traffic terms? | TRUE
[8 empty] | C | 17.7285 | m²/s² |  | Traffic pressure | 2.5089 | Pa |  | Valid wind? | TRUE
|  | Jet fan input | [5 empty] | det | 189.3249 | m/s |  | Jet fan pressure | 10.4521 | Pa |  | Check of values in the jet fan terms
| Count of fans | 1 | — | Calculation (vehicles faster than air) |  |  |  | v | 1.3641 | m/s |  | Sum of pressures (or 42) | 0 | Pa |  | '=AND(ISNUMBER(B28), B28 >= 0) | TRUE
| Static thrust | 730 | N at 1.2 kg/m³ |  | Air velocity | 1.3641 | m/s |  |  |  |  | Use this result? | TRUE |  |  | '=AND(ISNUMBER(B29), B29 >= 0) | TRUE
| Jet velocity | 30 | m/s |  | Volume flow | 68.2064 | m³/s |  | Calculation (reverse airflow) |  |  |  | Check calc of pressures |  |  | '=ISNUMBER(B30) | TRUE
| Installation efficiency | 0.75 | — |  |  |  |  | A | 4.7444 | — |  | Friction pressure | 159.12 | Pa |  | '=AND(ISNUMBER(B31), B31 >= 0) | TRUE
|  |  |  | Independent check calc of pressures |  |  |  | B | -12.2328 | m/s |  | Wind pressure | 10 | Pa |  | Valid jet fans? | TRUE
[5 empty] | Friction pressure | -2.961 | Pa | C | 17.7285 | m²/s² |  | Traffic pressure | 65.4847 | Pa |  |  |  | Valid input? | TRUE
[5 empty] | Wind pressure | -10 | Pa | det | -186.8024 | m/s |  | Jet fan pressure | -7.3 | Pa |  |  |  | Reason for invalid input: | dud equations
[5 empty] | Traffic pressure | 2.5089 | Pa | v | 10 | m/s |  | Sum of pressures (or 42) | 227.3047 | Pa
[5 empty] | Jet fan pressure | 10.4521 | Pa |  |  |  |  | Use this result? | FALSE
[5 empty] | Sum of pressures | 0 | Pa
A function to remove the path of a sheet tab name in LibreOffice. This is fragile.
[10 empty] | Filename: | C:\Users\clcp12\Desktop\[slug-flow-quadratic-020.xlsx]quadratics
[10 empty] | Directory separator: | /
Now strip off up to 100 strings ending in the directory separator.
[10 empty] | 1st pass | #VALUE!
[10 empty] | 2nd | #VALUE!
[10 empty] | 3rd | #VALUE!
[10 empty] | and so on. | #VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
#VALUE!
[10 empty] | Spreadsheet name in LibreOffice: | #VALUE!
[10 empty] | Spreadsheet name in Excel: | [slug-flow-quadratic-020.xlsx]quadratics
[10 empty] | Which program is editing this spreadsheet? | Excel
[10 empty] | Spreadsheet name to use: | [slug-flow-quadratic-020.xlsx]quadratics
Note on G24: If you set “Y” here, the drag figures will be divided by the standard wind tunnel blockage correction factor of (1 – A_veh/A_tunnel)^2, causing an increase in traffic drag.

## licence
Licence
Copyright (c) 2020-2021, Ewan Bennett (ewanbennett@fastmail.com)
All rights reserved.
Released under the BSD 2-clause licence (SPDX identifier: BSD-2-Clause):
Redistribution and use in source and binary forms, with or without modification, are
permitted provided that the following conditions are met:
1 | Redistributions of source code must retain the above copyright notice, this list
of conditions and the following disclaimer.
2 | Redistributions in binary form must reproduce the above copyright notice, this
list of conditions and the following disclaimer in the documentation and/or
other materials provided with the distribution.
THIS SOFTWARE IS PROVIDED BY THE COPYRIGHT HOLDERS AND CONTRIBUTORS "AS
IS” AND ANY EXPRESS OR IMPLIED WARRANTIES, INCLUDING, BUT NOT LIMITED TO,
THE IMPLIED WARRANTIES OF MERCHANTABILITY AND FITNESS FOR A PARTICULAR
PURPOSE ARE DISCLAIMED. IN NO EVENT SHALL THE COPYRIGHT HOLDER OR
CONTRIBUTORS BE LIABLE FOR ANY DIRECT, INDIRECT, INCIDENTAL, SPECIAL,
EXEMPLARY, OR CONSEQUENTIAL DAMAGES (INCLUDING, BUT NOT LIMITED TO,
PROCUREMENT OF SUBSTITUTE GOODS OR SERVICES; LOSS OF USE, DATA, OR
PROFITS; OR BUSINESS INTERRUPTION) HOWEVER CAUSED AND ON ANY THEORY OF
LIABILITY, WHETHER IN CONTRACT, STRICT LIABILITY, OR TORT (INCLUDING
NEGLIGENCE OR OTHERWISE) ARISING IN ANY WAY OUT OF THE USE OF THIS
SOFTWARE, EVEN IF ADVISED OF THE POSSIBILITY OF SUCH DAMAGE.